| [LOGO] | Risk Assessment | [DOC REF] Legionella |
| --- | --- | --- |

| Company | [COMPANY NAME] | Assessment Ref. | [DOC REF] |
| --- | --- | --- | --- |
| Assessment Title | Legionella | Revision | [REV] |
| Assessed By | [ASSESSOR NAME / ROLE] | Assessment Date | [DATE] |
| Location / Scope | [LOCATION / SCOPE] | Review Date | Within 12 months or on significant change |

Risk Rating Methodology (5 × 5): Risk = Likelihood × Severity

| L ↓ / S →; 1; 2; 3; 4; 5. 5; 5; 10; 15; 20; 25. 4; 4; 8; 12; 16; 20. 3; 3; 6; 9; 12; 15. 2; 2; 4; 6; 8; 10. 1; 1; 2; 3; 4; 5. | Low (1-4); Acceptable - maintain existing controls and monitor.. Medium (5-9); Tolerable - reduce so far as is reasonably practicable.. High (10-15); Substantial - additional controls required before proceeding.. Very High (16-25); Intolerable - stop activity; immediate action required.. |
| --- | --- |

Legionella Risk Assessment

Initial Risk = risk before / with baseline controls.  Residual Risk = risk once all listed controls are in place.

| Ref | Hazard | Who might be harmed & how | L | S | R | Control measures | L | S | R | Action owner / target |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| L1 | Exposure to Legionella bacteria in the water system | Staff, visitors and contractors - Legionnaires’ disease (potentially fatal) or Pontiac fever from inhaling contaminated aerosols; greater risk to older or immunosuppressed persons. | 3 | 5 | 15 | - Legionella risk assessment carried out by a competent person to ACOP L8 / HSG274 - Written scheme of control in place - Responsible person appointed - Hot water stored above 60°C and distributed above 50°C; cold water below 20°C - Review the L8 risk assessment on schedule and after any system change - Maintain temperature monitoring records | 1 | 5 | 5 | [OWNER / DATE] |
| L2 | Stagnation in infrequently used outlets | Staff and visitors - bacterial proliferation and aerosol exposure from little-used taps and dead legs. | 3 | 4 | 12 | - Little-used outlets flushed weekly and recorded - Redundant pipework (dead legs) removed where identified - Maintain the weekly flushing log - Identify and remove any remaining dead legs | 1 | 4 | 4 | [OWNER / DATE] |
| L3 | Scale and biofilm in outlets and components | Staff and visitors - bacterial growth in TMVs, spray taps and shower heads. | 2 | 4 | 8 | - TMVs serviced and descaled to schedule - Shower heads (where fitted) cleaned and descaled quarterly - Spray taps included in the monitoring regime - Confirm all wet outlets are on the asset register | 1 | 4 | 4 | [OWNER / DATE] |
| L4 | Stored hot water below control temperature | Staff and visitors - proliferation in water heaters / calorifiers running too cool. | 2 | 5 | 10 | - Stored hot water maintained above 60°C - Calorifier flow above 60°C and return above 50°C - Monthly temperature checks at sentinel outlets - Log monthly calorifier and sentinel outlet temperatures - Act on any out-of-range readings | 1 | 5 | 5 | [OWNER / DATE] |
| L5 | Inadequate management arrangements / competence | All occupants - failure of the control scheme through lack of competent oversight. | 2 | 4 | 8 | - Duty holder and responsible person appointed and trained - Competent water treatment contractor engaged - Logbook and records maintained - Refresh responsible person training - Keep the logbook current | 1 | 4 | 4 | [OWNER / DATE] |
| L6 | Stagnation following low occupancy or shutdown | Staff and visitors - proliferation after prolonged vacancy or system shutdown. | 2 | 4 | 8 | - Flushing regime covers low-occupancy periods - System recommissioned to HSG274 after any shutdown - Flush and, if required, disinfect after any prolonged vacancy before reoccupation | 1 | 4 | 4 | [OWNER / DATE] |

This risk assessment must be reviewed within 12 months, following any incident or near miss, on significant change to the premises, staff, equipment or working practices, or where there is reason to believe it is no longer valid.

| Assessed by (sign) | Date | Reviewed by (sign) | Date |
| --- | --- | --- | --- |